[image: image17.jpg]SURETRON B

Professional manufacturer of dimmable driver in China





Triac/0-10V/1-10V/Potentiometer/10V PWM 5 in 1  Dimmable LED driver  600W


KVG-DWJ Series 600W

Whole Family: KVG-XX600-DWJ (xx=24V 36V 48V) - [ 30W 60W 80W 96W 100W 120W 150W 200W 300W 500W 600W]

[image: image1.png](UL )us

LISTED
E495946



 [image: image2.png]


 [image: image3.png]TYPE HL



 [image: image4.png]SELV



 [image: image5.png]RoHS



 [image: image6.png]Reach




[image: image7.png]




	Features
	

	Output: 
	Constant Voltage

	Range:
	110-277VAC

	PFC design:
	Built-in active PFC function

	Efficiency:
	Up to 93.5%

	Protections:
	Short circuit/ over load/ over temperature

	Heat dissipation:
	Cooling by free air convection

	Waterproof performance:
	Driver built-in Junction box, For dry, damp and wet locations

	Dimming function:
	Phase dimming: work with Forward phase , MLV and Reverse phase , ELV, TRIAC dimmers.  

0-10V dimming: 0-10V/1-10V/Potentiometer/10V PWM 4 in 1 

	Dimming range:
	0-100%

	Application:
	Suitable for LED lighting and moving sign applications

	Warranty:
	5 years warranty


Specification
	Model
	KVG-24600-DWJ
	KVG-36600-DWJ
	KVG-48600-DWJ

	Certificate
	UL / cUL / FCC / TYPE HL / SELV / RoHS / Reach

	Output
	DC Voltage
	24V
	36V
	48V

	
	Voltage Tolerance
	±0.5V

	
	Voltage Regulation
	≤0.5%

	
	Rated current
	25A
	16.67A
	12.5A

	
	Rated power
	600W

	
	Load Regulation
	≤1%

	Input
	Voltage Range
	110-277VAC

	
	Frequency Range
	47 - 63Hz

	
	Power Factor @ full load
	PF≥0.95@110VAC;  PF≥0.93@277VAC

	
	THD(Typ.) @ full load
	≤10%@120VAC

	
	Efficiency @ full load
	90.5%@120VAC

93.45%@277VAC
	90.5%@120VAC

93.45%@277VAC
	90.5%@120VAC

93.45%@277VAC

	
	Standby power
	＜0.5W

	
	AC Current (Max.)
	6A@110VAC

	
	Inrush Current (Typ.)
	52A, 810us@50%110VAC     76A, 148us@50%277VAC

	
	Leakage current
	<0.5mA

	Protection
	Short Circuit
	Hiccup mode, recovers automatically after fault condition is removed

	
	Over Load
	≦120% Hiccup mode, recovers automatically after fault condition is removed

	
	Over temperature
	Shell surface temp.100℃±10℃ shut down o/p voltage, automatically recover after drops.

	Environment
	Working TEMP.
	-40~+60℃ (see below derating curve)

	
	Working Humidity
	20 - 95%RH  non-condensing

	
	Storage TEM.,Humidity
	-40 - +80℃,10 - 95% RH non-condensing

	
	TEMP.coefficient
	±0.03%/℃(0 - 50℃) 

	
	Vibration
	10~500Hz, 5G 10min./1 cycle, period for 60min. each along X,Y,Z axes

	Safety & EMC
	Safety standards
	UL8750 CAN/CSA-C22.2 No. 250.13 (US) 

	
	Withstand voltage
	I/P-O/P: 1.8KVAC   I/P-FG: 1.8KVAC  O/P-FG1.8KVAC

	
	Isolation resistance
	I/P-O/P: 100MΩ / 500VDC / 25℃ / 70% RH

	
	EMC Emission
	FCC Part 15, Subpart B; ANSIC63.4-2017 (US) 

	
	EMC Immunity
	FCC/ICES do not request this test (US)

	Others
	Net Weight
	2.8KG

	
	Dimension
	280*140.2*50.2mm(L*W*H)

	
	Packing
	342*285*170mm    5pcs /CTN  

	Notes
	All parameters NOT specially mentioned are measured at 120VAC input, rated load and 25℃of ambient temperature.

Tolerance: includes set up tolerance and load regulation .


Efficiency Curve (efficiency vs output load)
[image: image8.png]efficiency curve
sasn

ot S — ———1
e

93.4% 4—_
e
o
e
B = o s e
i

50%  60%  70%  80%  90%  100%
load

—e— KVG-0B00-DW 120V —e— KVG-Xx600-DW 277V





Power factor curve

[image: image9.png]Power factor curve:

™
96 S S S

092

088

084

080
s0% 6%  70%  80%  O0%  100%
load

—e— KVG-xxB00-DWJ 120V —8— KVG-x600-DWJ 277V





Derating Curve (output load vs TEMP.)

[image: image10.png]7l (%)
LOAD(%)

SRR

Load derating curve

| L 1 1 | | L
“40°C -20°C 0°C 10°C_20°C 30°C_40°C 50°C 60°C  70°C
Ambient Temperature (°C)

TR (°C)




To extend their life, please refer to the Derating Curve and derate according to the temperature.
Please note that the rise in temperature of LED fixtures over a long period of time will cause their power to rise. 

Therefore, we recommend the power supply to reserve a certain amount of load to avoid overloading .

Mechanical Specification

[image: image11.png]NO. DESCRIPTION REASON DATE MODIFIER
1 u___  _—_—§—{GM \—

'10. 3150
262. 0

11. 0236
280. 0

— ]
|
| —

00 O 00&,

10. 1482]
257. 8

— {
— L
@p)

Lo L
O Tt
-
L1 __‘Iu

Fﬂ%gﬁﬁ X Fﬂ%éﬁﬁg X
PRODUCT NAME PRODUCT No.

T AR
;820220300 | EFEE T Mool | S| ton
EN L

CHECKED MATERIAL REV
- P WS AL
APPROVED DRAWING No SCALE
= 10 A LA @ AT .
S R e |u [
OLERANCE 10~20mm| =+ 1. Omm

=t pe A Ihufal Shengehiong Eecironics Co,
| 0~5 mm| 0. 5mm | Rl EE T ARAA






	American wire gauge

	JM600

	Input wire
	Black(L) White(N) Green(G)(3*18AWG)

	Output wire(24V&36V&48V)
	Red(V+) Black(V-)(2*14AWG)
Red(V+) Black(V-)(2*14AWG)

	Dimming wire
	Purple(D+) Pink(D-)(2*18AWG)

	Remarks：Please make sure your connect these correctly otherwise your product will not function correctly and could be damaged


Warm tips:

Recommended Max. Carrying Current (A) = wire diameter(mm²) x 10A/mm ²

For example: 1mm ² output cable, Recommended Max. Carrying Current (A) = 1mm ² x 10A/mm ²=10A

Any other requests for cable, we can customize.

Dimming Operation and Connecting Diagram  
Using two ways of dimming at the same time, you must be assured that LED lighting is up to the max. Brightness then you could operate with the other dimming;

[image: image12.png]Triac & 0/1-10V

Triac Dimmer
O
G J:‘_ {0000)
L
AC~ N o

®DZr

Red
Black
Black . .
White Dimmable LED Driver
Green
Purple

Pink

V+
V-

DIM+
DIM -

0/1-10V Dimmer

©)

{oo000)>

L o—
AC~ N o
LED G=
=1 =1 12 ‘
<3 I





Using one dimming ---TRIAC/Phase cut dimming
The Pulse-Width Modulation (PWM) of output voltage can be adjusted through input terminal of the AC phase line(L) by connection

a phase /Triac dimmer or lighting system.

Working with Forward phase, MLV and Reverse phase , ELV, TRIAC dimmers or light system. 

Min. loading is about 10%.
Please try to use dimmers with power at least 1.5 times as the output power of the driver. 

[image: image13.png]Triac
(KVG series)

Triac Dimmer
O
GJE_ {0000
AC~ g o

®DZr

Black
White Dimmable LED Driver
Green

Red
Black

Purple
Pink

V+
v -

DIM+
DIM -

LED





Using one dimming ---0-10/ 1-10V/ 10V PWM/ Potentiometer dimming
[image: image14.png]0-10V Dimmer
10V PWM Dimmer

_ 0-10V/10V PWM oo b —
ON / OFF Switch N (o000>
LED G=
©) r
L Red | V+
- 1 % %
1 L L | Black ) ) Black | V o
N | White Dimmable LED Driver
I G Green

G= Purple | DIM+

Pink | DIM-





[image: image15.png]0/1-10V Dimmer

0/1-10V

©)

Dimmable LED Driver





[image: image16.png]1-10V / Potentiometer

ON / OFF Switch
|
— ©
G=
L
N o

DzZzr

Black
White
Green

Red
Black
Dimmable LED Driver

Purple
Pink

V+
V-

DIM+
DIM -

LED

1-10V Dimmer
Potentiometer Dimmer

{ooo0o0)>

N
N





Instruction
This driver should be installed by qualified and professional person.
Please make sure the driver is installed with adequate ventilation around it to allow for heat dissipation.

Ensure that wiring is correct before test in order to avoid light and power supply damage.
If driver Cannot work normally, don’t maintain privately.
Have any questions, please contact Zhuhai Shengchang.

Please visit our website or contact us for more information! www.scpower.net.cn/en
 SHAPE  \* MERGEFORMAT 


[image: image19.png]


     www.scpower.net.cn/en               info@scpower.net.cn                                                                               A/0 

[image: image17.jpg][image: image18][image: image19.png]